UNDERWRITERS LABORATORIES INC.	   		     APPLIANCE WIRING MATERIAL

Subj. 758    	Section 2      	Page 2464        Issued:  May 2, 1968

Revised:  Feb. 5, 2002

Style 2464		PVC Jacketed Cable.

______________________________________________________________________________

Rating		80°C, 300 V.

______________________________________________________________________________

Insulated		Labeled or complying with manufacturer's AWM Procedure

Conductors		having a minimum rating of 80°C and 300 V.

______________________________________________________________________________

Assembly		Two or more singles, twisted pairs of groups of twisted 				singles twisted together or singles or groups of singles

may be laid parallel to form flat, oval or round cable.

Lay not specified.  Barrier layer and/or fillers optional.  			Manufacturer shall maintain a complete description of each 				assembly.  May use same or mixed AWG size.

______________________________________________________________________________

Covering		(Optional) A 6 mil or heavier PVC covering may be extruded 				over the conductor assembly.

______________________________________________________________________________

Shield		Optional.

______________________________________________________________________________

Jacket		PVC - Class 43

THICKNESS OF PVC JACKET (mils)

#Dia. of Cable					Minimum

Under Jacket		Minimum		at any

in Inches.   		Average		 point

0.700 or less		   30		  	24

0.701 - 1.000		   45		  	36

1.001 - 1.500		   60		  	48

1.501 - 2.500		   80		  	64

2.501 - 4.000		  110		  	88

4.001 or larger	  	  140		 	112

# Major dia if cable is flat or oval.

______________________________________________________________________________

*Braid		Optional.

______________________________________________________________________________

Standard		Appliance Wiring Material UL 758.

______________________________________________________________________________

(Continued on Page 2464A)

UNDERWRITERS LABORATORIES INC.	   		    APPLIANCE WIRING MATERIAL

Subj. 758		Section 2		Page 2464A 	    Issued:  May 2, 1968

Revised:  Jan. 8, 2001

Instructions	Detailed Examination of the cable assembly and jacket.

*to UL		Physical Properties of Jacket.

Representative	Dielectric Strength Test, 1500 Volts, (Shielded cable only). 						*

The designation of all Styles of the individual conductors 				   used making up the cable assembly shall be available, and 			   the UL Representative’s tag shall indicate if the Style 				   is labeled or not.  If they are not labeled, the 					   appropriate Follow-Up Tests shall be conducted.

______________________________________________________________________________

UL			(4)  Detailed Examination.

*Counter-Check	(4)  Physical Properties of Jacket.

*Program		(4)  Heat Shock on Jacket.

(4)  Deformation on Jacket, Class 43.

*			(4)  Cold Bend on Completed Cable.

*			(4)  Vertical Flame Test on Completed Cable.

If the insulated styles are not labeled, the appropriate 				Follow-Up Tests shall be conducted.

______________________________________________________________________________

*Marking		General.

______________________________________________________________________________

Use			Internal wiring or external interconnection of electronic 				equipment (such as desk-type calculators, dictating 					machines, or x-ray equipment).